{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["报价清单"],"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"报价清单","index":0,"n_rows":59,"n_cols":7,"rows_kept":59,"merged":[[0,0,0,6],[1,0,1,6],[2,0,2,6],[10,1,10,4],[11,0,11,6],[12,0,12,6],[23,1,23,3],[23,4,23,5],[24,0,24,6],[30,6,33,6],[42,6,43,6],[44,6,45,6],[52,1,52,3],[52,4,52,5],[53,1,53,3],[53,4,53,5],[56,4,56,5],[57,0,57,3],[57,4,57,5],[58,0,58,6]],"flags":["formulas_cached_only"]}
["翔安体育交流中心充电项目估算清单"]
["一、设备部分"]
["1.主材清单"]
["序号","项目名称、特征","单位","数量","综合单价","合价","备注"]
[1,"800KVA箱式变电站（终端型）","台",1,null,{"v":0,"d":"0.00"},"1.含运费\n2.含税\n3.S-20油浸式全铜变压器\n4.符合GB-20052-2020、GB1094.1-2013、GB/T6451 二级能耗标准"]
[2,"落地式配电箱","台",1,null,{"v":0,"d":"0.00"},"1.含运费\n2.含1个4P-D250开关、8个2P-C63开关、4个2P-C16开关等\n3.户外式；材质：304不锈钢"]
[3,"YJLHV-0.6/1KV 3*150+2*70mm2","M",160,null,{"v":0,"d":"0.00"},"1.含运费\n2.含税\n3.电缆双拼\n4.符合国标GB/T 31840-2015"]
[4,"YJLHV-0.6/1KV 4*150+1*70mm2","M",170,null,{"v":0,"d":"0.00"},"1.含运费\n2.含税\n3.符合国标GB/T 31840-2015"]
[5,"YJLHV-0.6/1KV 3*50+2*25mm2","M",35,null,{"v":0,"d":"0.00"},"1.含运费\n2.含税\n3.符合国标GB/T 31840-2015"]
[6,"YJV-3*6mm2","M",130,null,{"v":0,"d":"0.00"},"1.含运费\n2.含税\n3.符合国标GB/T 12706.1-2020"]
[null,"主材小计：(元）",{"$nulls":3},{"v":0,"d":"0.00"},"含税"]
["二、施工部分"]
["1、高压部分"]
["序号","项目名称、特征","单位","数量","综合单价/指导价\n","合价","备注"]
[1,"箱变安装","项",1,null,{"v":0,"d":"0.00"},"含设备吊装卸货、二次搬运、开箱检查，本体就位，器身检查，垫铁及止轮器制作、安装，附件安装，接地、补漆，单体调试"]
[2,"箱变基础制作","项",1,null,{"v":0,"d":"0.00"}]
[3,"箱变接地系统","项",1,null,{"v":0,"d":"0.00"}]
[4,"箱变调试、试验、送电","项",1,null,{"v":0,"d":"0.00"}]
[5,"设计费","项",1,null,{"v":0,"d":"0.00"},"含施工图、竣工图等成套设计图纸"]
[6,"箱变围栏","米",30,null,{"v":0,"d":"0.00"},"箱变围栏：1、材质：304不锈钢"]
[7,"箱变标准化:(安全器具：绝缘手套、绝缘靴、操作棒、接地线\\标准化的图文内容：电缆及设备标书牌、二次接线图等)","项",1,null,{"v":0,"d":"0.00"}]
[8,"热缩户内终端头制作，3*70mm2-120mm2","个",1,null,{"v":0,"d":"0.00"},"高压电缆头制作（热缩套管，压接线鼻子、绝缘胶带、孔洞防火泥封堵）"]
[9,"协调费","项",1,null,{"v":0,"d":"0.00"}]
[null,"单项小计",null,null,{"v":0,"d":"0.00"}]
["1、低压部分"]
["序号","项目名称、特征","单位","数量","综合单价/指导价","合价","备注"]
[1,"绿化带，开挖断面500*700mm","m",45,null,{"v":0,"d":"0.00"},"1.绿化带草皮恢复\n2.清运"]
[2,"PVC管埋地敷设，规格：DN110，壁厚3mm","m",190,null,{"v":0,"d":"0.00"},"电缆保护管敷设（配管、锯管、煨弯、管口处理、接管、埋设、接管口）"]
[3,"PVC管埋地敷设，规格：DN50，壁厚2mm","m",170,null,{"v":0,"d":"0.00"},"电缆保护管敷设（配管、锯管、煨弯、管口处理、接管、埋设、接管口）"]
[4,"PVC管埋地敷设，规格：DN32，壁厚2mm","m",170,null,{"v":0,"d":"0.00"}]
[5,"电缆敷设：YJLHV-3*150+2*70mm2","M",160,null,{"v":0,"d":"0.00"},"电缆保护管敷设（配管、锯管、煨弯、管口处理、接管、埋设、接管口）"]
[6,"电缆敷设：YJLHV- 4*150+1*70mm2","M",170,null,{"v":0,"d":"0.00"}]
[7,"电缆敷设：YJLHV- 3*50+2*25mm2","M",35,null,{"v":0,"d":"0.00"}]
[8,"电缆敷设：YJV-3*6mm2","M",130,null,{"v":0,"d":"0.00"}]
[9,"热缩终端头制作，150mm2内 五芯","套",34,null,{"v":0,"d":"0.00"}]
[10,"480kW整流柜安装（含现场卸货）","个",2,null,{"v":0,"d":"0.00"}]
[11,"配电箱安装","个",1,null,{"v":0,"d":"0.00"}]
[12,"分体式终端安装（含现场卸货）","座",8,null,{"v":0,"d":"0.00"}]
[13,"立杆式交流慢充设备安装","个",6,null,{"v":0,"d":"0.00"}]
[14,"C25砼浇筑基础，规格：1350*1200*600mm，高出地坪：200mm","座",2,null,{"v":0,"d":"0.00"},"充电桩基础及箱体安装（人工挖基坑、基地夯实、浇筑混凝土垫层、浇筑混凝土基础、预埋件、回填土、箱体安装、固定预埋件、设备安装含接线）\n"]
[15,"C25砼浇筑基础，规格：600*600*600mm，高出地坪：200mm","座",19,null,{"v":0,"d":"0.00"},"1.充电桩基础及箱体安装（人工挖基坑、基地夯实、浇筑混凝土垫层、浇筑混凝土基础、预埋件、回填土、箱体安装、固定预埋件、设备安装含接线）\n2.含8个直流终端基础、6个交流充电桩基础、1个配电箱基础、4个路灯基础"]
[16,"（充电桩、配电箱、箱变等）基础表面刷漆，灰色图漆","项",1,null,{"v":0,"d":"0.00"},"基础表面处理和美化"]
[17,"接地扁铁，热镀锌—50X5mm（箱变接地和充电桩接地网连接，）","米",80,null,{"v":0,"d":"0.00"},"防雷接地（设计电阻<4Ω）"]
[18,"接地极（50*5*2500mm镀锌角钢）","根",8,null,{"v":0,"d":"0.00"}]
[19,"磷酸铵盐干粉灭火器（35公斤）手推式","组",1,null,{"v":0,"d":"0.00"},"消防设施"]
[20,"磷酸铵盐干粉灭火器（2*5公斤）手提式","组",4,null,{"v":0,"d":"0.00"}]
[21,"砖砌1080*1080*1000，铸铁轻型井盖","口","3",null,{"v":0,"d":"0.00"},"手孔井和电缆工井（人工挖基坑、基地夯实、浇筑混凝土垫层、砌筑砖基础、四周抹灰、回填土、安装井盖）"]
[22,"RVV 2*4mm","米",170,null,{"v":0,"d":"0.00"},"含敷设"]
[23,"rvvsp 2*1.5mm","米",170,null,{"v":0,"d":"0.00"},"含敷设"]
[24,"休息室","项","1",null,{"v":0,"d":"0.00"},"1、配置铁质四人餐桌：2套；\n2、配置1.5匹及以上空调（需能通过远程设置开启、关闭功能）；\n3、配置照明电源插座等；\n4、尺寸不小于6m*3m*2.3m；\n5、含底座、基础"]
[25,"监控照明系统","套","1",null,{"v":0,"d":"0.00"},"1、含400万POE臻全彩高清网络枪型摄像机4组、8路硬盘录像机一组\n2、监控专用硬盘,4T两只\n3、8口POE交换机一只\n4、监控平台\n5、照明设施4根含施工安装（照明品牌采用通士达照明）\n6、其他辅材弱电箱\n7、含基础、安装、接地等所有工序     \n8、照明电源采用RVV-2*2.5，网线采用超五类网线，需配置定时器                                    \n9、含3年宽带或3年流量卡，流量卡1年不少于1000G"]
[26,"卫生间","项","1",null,{"v":0,"d":"0.00"},"1、配置男女分开式厕所；\n2、男卫配置2个及以上蹲位、站位2个及以上；\n3、女卫配置2个及以上蹲位；\n4、配置洗手池；\n5、配置化粪池；\n6、配置照明冲水系统等；\n7、方案需经过业主单位确认后方可实施；\n8、含踏步、底座基础\n9、高出地坪：300mm"]
[null,"单项小计",null,null,{"v":0,"d":"0.00"}]
[null,"单项合计",null,null,{"v":0,"d":"0.00"}]
[1,"安全文明施工费","项",1,0.03,{"v":0,"d":"0.00"},"完工后应对场地进行清扫、清洁"]
[2,"税金（施工安装）","项",1,0.09,{"v":0,"d":"0.00"}]
[3,"施工部分合计","项",1,{"v":0,"d":"0.00"}]
["项目总计(一)+（二）",{"$nulls":3},{"v":0,"d":"0.00"},null,"含税"]
["报价单位：                 报价人：                        联系方式："]